## System Calculation
SYSTEM CALCULATOR DETNOV CAD-150 EXCEL TOOL | [8 empty] | SC 116 en 2019 i
Fill the field for the maximum % of devices in alarm at the same time (Yelow field)
Time backup power supply | [6 empty] | Maximum devices in alarm at the same time
Standby time | 24 | h | Select standby time |  |  |  | Detectors | Max.10/loop
Alarm time | 30 | min | Select alarm time |  |  |  | MCP | 10%
| Note: this value does not comply with EN 54 | [5 empty] | Sounders/Strobes | 100%
System Parameters | [6 empty] | Modules | 100%
CAD_150_1 | 0.16 | 0.2 | Select control panel from the list
BTD-1212 | 12 | 12 | Select battery from the list
| I_Standby (A) | I_Alarm (A)
Panel auxilliary 24VCC output
Panel sounder output 1
Pantel sounder output 2
I_Total_Standby | 0.16 | A |  | Minimum battery needed |  |  | Battery Time*
I_Total_Alarm | 0.2 | A |  | 4.925 |  |  | 2 x 7,2 Ah | 2 x 12 Ah** | 2 x 18 Ah | 2 x 24 Ah
1,25 Cmin | 4.925 | 3.94 | 5 |  |  |  | 36.875 | 59.375 | 89.375 | 119.375
Selected battery | OK |  | 4 |  |  |  | *Battery time: Standby time + Alarm mode time
| FALSE | [5 empty] | **BTD-1212 only available for CAD-150-2-MB and CAD-150-4
Fill the PCS field if panel has extension card (Yellow field)
Loop | I_Standby (A) | I_Alarm (A) |  | Extension Cards | PCS | I_Standby (A) | I_Standby (A)
Loop 1 | 0 | 0 |  | TRED-150 | 0 | 0.05 | 0
Loop 2 | 0 | 0 |  | TMB-151 | 0 | 0.05 | 0
Loop 3 | 0 | 0 |  | TMBFI-151 | 0 | 0.05 | 0
Loop 4 | 0 | 0 |  | TMB-251 | 0 | 0.05 | 0
Loop 5 | 0 | 0 |  | TMBFI-251 | 0 | 0.05 | 0
Loop 6 | 0 | 0 |  | TED-151-CL | 0 | 0.05 | 0
Loop 7 | 0 | 0 |  |  | 0 |  | 0
Loop 8 | 0 | 0
Total | 0 | 0
This tool may be used as a design help for Detnov Security S.L. We reserve the right not to be responsible for its accuracy, completeness or quality of the information provided, including any kind of information which could be incomplete or incorrect.

## Datos (hidden)
Características centrales |  |  |  | Características baterías
Central |  | I_Reposo (A) | I_Alarma (A) |  | Voltaje (V) | Capacidad (Ah) |  |  | TABLA AUXILIAR
CAD-150-1 & CAD-150-1-Mini | CAD_150_1 | 0.16 | 0.2 | BTD-1207 | 12 | 7.2 | 24 | BTD-1224 | Centrales
CAD-150-2 | CAD_150_2 | 0.22 | 0.255 | BTD-1212 | 12 | 12 | 18 | BTD-1218 |  | CAD_150_1 | CAD_150_2 | CAD_150_2_MB | CAD_150_4 | CAD_150_8_4loop | CAD_150_8_6loop | CAD_150_8_8loop | CAD_150_8PLUS_4loop | CAD_150_8PLUS_6loop | CAD_150_8PLUS_8loop | CAD_150_4_P | CAD_150_8PLUS_P_4loop | CAD_150_8PLUS_P_6loop | CAD_150_8PLUS_P_8loop
CAD-150-2-MB | CAD_150_2_MB | 0.26 | 0.3 | BTD-1218 | 12 | 18 | 12 | BTD-1212 | CAD_150_1 | BTD-1207 | BTD-1207 | BTD-1207 | BTD-1207 | BTD-1207 | BTD-1207 | BTD-1207 | BTD-1207 | BTD-1207 | BTD-1207 | BTD-1207 | BTD-1207 | BTD-1207 | BTD-1207
CAD-150-4 | CAD_150_4 | 0.3 | 0.34 | BTD-1224 | 12 | 24 | 7.2 | BTD-1207 | CAD_150_2 |  |  | BTD-1212 | BTD-1212 | BTD-1218 | BTD-1218 | BTD-1218 | BTD-1218 | BTD-1218 | BTD-1218 |  | BTD-1218 | BTD-1218 | BTD-1218
CAD-150-8 (4 lazos) | CAD_150_8_4loop | 0.3 | 0.34 | [5 empty] | CAD_150_2_MB | [7 empty] | BTD-1224 | BTD-1224 | BTD-1224 |  | BTD-1224 | BTD-1224 | BTD-1224
CAD-150-8 (6 lazos) | CAD_150_8_6loop | 0.4 | 0.44 | [5 empty] | CAD_150_4
CAD-150-8 (8 lazos) | CAD_150_8_8loop | 0.5 | 0.54 | Características baterías |  |  |  |  | CAD_150_8_4loop
CAD-150-8-PLUS (4 lazos) | CAD_150_8PLUS_4loop | 0.3 | 0.34 | Cantidad tarjetas |  |  |  |  | CAD_150_8_6loop
CAD-150-8-PLUS (6 lazos) | CAD_150_8PLUS_6loop | 0.4 | 0.44 | 0 |  |  |  |  | CAD_150_8_8loop
CAD-150-8-PLUS (8 lazos) | CAD_150_8PLUS_8loop | 0.5 | 0.54 | 1 |  |  |  |  | CAD_150_8PLUS_4loop
CAD-150-4-P | CAD_150_4_P | 0.335 | 0.375 | [5 empty] | CAD_150_8PLUS_6loop
CAD-150-8-PLUS-P (4 lazos) | CAD_150_8PLUS_P_4loop | 0.335 | 0.375 | Sección cable | AWG |  |  |  | CAD_150_8PLUS_8loop
CAD-150-8-PLUS-P (6 lazos) | CAD_150_8PLUS_P_6loop | 0.435 | 0.475 | 0.5 | 21 |  |  |  | CAD_150_4_P
CAD-150-8-PLUS-P (8 lazos) | CAD_150_8PLUS_P_8loop | 0.535 | 0.575 | 0.8 | 20 |  |  |  | CAD_150_8PLUS_P_4loop
|  |  |  | 1 | 18 |  |  |  | CAD_150_8PLUS_P_6loop
|  | Tiempos según normativa |  | 1.5 | 16 |  |  |  | CAD_150_8PLUS_P_8loop
|  | Reposo (h) | Alarma (min) | 2 | 15
|  | 72 | 30 | 2.5 | 14 |  |  |  | TABLA AUXILIAR 2: para condición de batería necesaria
|  | 48 | 15
|  | 30 | 5 | [5 empty] | Centrales
|  | 24 | 0 | [5 empty] | CAD_150_1 | BTD-1207
|  | 4 |  | Fuentes alimentación: |  |  |  |  | CAD_150_2 | BTD-1207
|  |  |  | 120 | BTD-12120 |  |  |  | CAD_150_2_MB | BTD-1207
|  |  |  | 38 | BTD-1244 |  |  |  | CAD_150_4 | BTD-1207
|  |  |  | 17 | BTD-1218 |  |  |  | CAD_150_8_4loop | BTD-1207 | BTD-1218
[9 empty] | CAD_150_8_6loop | BTD-1207 | BTD-1218
|  |  |  | CAD_150_1 | 0.16 | 0.2 |  |  | CAD_150_8_8loop | BTD-1207 | BTD-1218
|  |  |  | BTD-1212 | 12 | 12 |  |  | CAD_150_8PLUS_4loop | BTD-1207 | BTD-1218 | BTD-1224
[9 empty] | CAD_150_8PLUS_6loop | BTD-1207 | BTD-1218 | BTD-1224
|  |  |  | Minimum battery needed |  | Dif. Entre BTD y Minimum battery needed |  |  | CAD_150_8PLUS_8loop | BTD-1207 | BTD-1218 | BTD-1224
|  |  |  | 4.925 |  | -7.075 | 3 |  | CAD_150_4_P | BTD-1207
[6 empty] | PS necesaria: | BTD-1218 |  | CAD_150_8PLUS_P_4loop | BTD-1207 | BTD-1218 | BTD-1224
[9 empty] | CAD_150_8PLUS_P_6loop | BTD-1207 | BTD-1218 | BTD-1224
[9 empty] | CAD_150_8PLUS_P_8loop | BTD-1207 | BTD-1218 | BTD-1224
Para ocultar valores en celda: formato de numero. En el cuadro tipo escribir ;;; (3 puntos y coma)

## SC_Loop 1
SYSTEM CALCULATOR DETNOV CAD-150 EXCEL TOOL | [11 empty] | SC 116 en 2019 i
Loop | [9 empty] | System Check
Section of wire | 1.5 | 16 | [7 empty] | Current |  | OK
Lenght loop | 1000 | meters | [7 empty] | Addresses |  | OK
Fill Cable Section in mm2 and the Line Distance in meters (Yelow field)
|  | Fill the PCS field for the desired configuration (Yelow field) | Fill the PCS field for the desired configuration (Yelow field)
Devices Loop 1
REF. | Description | PCS | I_Standby (A) | I_Standby (A) | PCS_alarm | I_Alarm (A) | I_Alarm (A) | I_Sounders (A) | DET | MOD | SND | ADR
DOD-220A | Addressable smoke detector |  | 0.0001272 | 0 | 0 | 0.00361 | 0
DOD-220A-I | Addressable smoke detector with isolator |  | 0.0001958 | 0 | 0 | 0.00374 | 0
DOTD-230A | Addressable smoke and heat detector |  | 0.0001416 | 0 | 0 | 0.0036 | 0
DOTD-230A-I | Addressable smoke and heat detector with isolator |  | 0.0002124 | 0 | 0 | 0.00374 | 0
DTD-210A | Addressable heat detector |  | 0.0001222 | 0 | 0 | 0.00364 | 0
DTD-210A-I | Addressable heat detector with isolator |  | 0.0001924 | 0 | 0 | 0.00376 | 0
DTD-215A | Addressable high temperature detector |  | 0.0001337 | 0 | 0 | 0.00378 | 0
DTD-215A-I | Addressable high temperature detector with isolator |  | 0.0002035 | 0 | 0 | 0.00377 | 0
DGD-600 | Stand-alone natural gas detector (24V) |  | 0.00218 | 0 | 0 | 0.00222 | 0
DGD-600-AC | Stand-alone natural gas detector (230V) |  | 0.0026 | 0 | 0 | 0.00316 | 0
DGD-620 | Stand-alone LPG detector (24V) |  | 0.00218 | 0 | 0 | 0.00222 | 0
DGD-620-AC | Stand-alone LPG detector (230V) |  | 0.0026 | 0 | 0 | 0.00316 | 0
DBD-70A | Addressable lineal smoke detector |  | 0.038 | 0 | 0 | 0.038 | 0
MAD-401 & MAD-401-I | 1 output addressable module |  | 0.0002168 | 0 | 0 | 0.00306 | 0
MAD-402 & MAD-402-I | 2 outputs addressable module |  | 0.0002174 | 0 | 0 | 0.00595 | 0 |  |  | 0
MAD-405-I | 5 outputs addressable module |  | 0.0002786 | 0 | 0 | 0.00315 | 0 |  |  | 0
MAD-409-I | 10 outputs addressable module |  | 0.0003677 | 0 | 0 | 0.0033 | 0
MAD-411 & MAD-411-I | 1 input addressable module |  | 0.0001916 | 0 | 0 | 0.00306 | 0
MAD-412 & MAD-412-I | 2 inputs addressable module |  | 0.000191 | 0 | 0 | 0.00584 | 0 |  |  | 0
MAD-415-I | 5 inputs addressable module |  | 0.0001888 | 0 | 0 | 0.00395 | 0 |  |  | 0
MAD-419-I | 10 inputs addressable module |  | 0.0001892 | 0 | 0 | 0.00484 | 0 |  |  | 0
MAD-421 & MAD-421-I | 1 output/1 input addressable module |  | 0.0002101 | 0 | 0 | 0.00592 | 0 |  |  | 0
MAD-422 & MAD-422-I | 2 outputs/2 inputs addressable module |  | 0.000234 | 0 | 0 | 0.00591 | 0 |  |  | 0
MAD-425-I | 5 outputs/5 inputs addressable module |  | 0.000284 | 0 | 0 | 0.00408 | 0 |  |  | 0
MAD-429-I | 10 outputs/10 inputs addressable module |  | 0.0003766 | 0 | 0 | 0.005 | 0 |  |  | 0
MAD-431 & MAD-431-I | 1 output 24V addressable module |  | 0.000215 | 0 | 0 | 0.00361 | 0
MAD-432 & MAD-432-I | 2 outputs 24V addressable module |  | 0.0002033 | 0 | 0 | 0.0068 | 0
MAD-441 & MAD-441-I | 1 conventional zone addressable module |  | 0.0001878 | 0 | 0 | 0.00304 | 0
MAD-442 & MAD-442-I | 2 conventionals zones addressable module |  | 0.0001878 | 0 | 0 | 0.00584 | 0
MAD-450 & MAD-450-I | Addressable manual call point with isolator |  | 0.0001766 | 0 | 0 | 0.00303 | 0
MAD-451-I | Addressable manual call point with isolator |  | 0.0001774 | 0 | 0 | 0.003 | 0
MAD-461-I | Addressable sounder with isolator |  | 0.0001769 | 0 | 0 | 0.00835 | 0
MAD-464-I Low Volume (78 dB) | Addressable sounder with isolator |  | 0.0001765 | 0 | 0 | 0.01232 | 0
MAD-464-I Medium Volume (93 dB) | Addressable sounder with isolator |  | 0.0001765 | 0 | 0 | 0.01232 | 0
MAD-464-I High Volume (97 dB) | Addressable sounder with isolator |  | 0.0001765 | 0 | 0 | 0.01232 | 0
MAD-465-I Low Volume (78 dB) | Addressable sounder with beacon and isolator |  | 0.0001773 | 0 | 0 | 0.01232 | 0
MAD-465-I Medium Volume (93 dB) | Addressable sounder with beacon and isolator |  | 0.0001773 | 0 | 0 | 0.01232 | 0
MAD-465-I High Volume (97 dB) | Addressable sounder with beacon and isolator |  | 0.0001773 | 0 | 0 | 0.01232 | 0
MAD-564-I (loop) | Addressable sounder with isolator |  | 0.00158 | 0 | 0 | 0.02111 | 0
MAD-564-I (External PS) | Addressable sounder with isolator |  | 0.00035 | 0 | 0 | 0.0008 | 0
MAD-565-I (loop) | Addressable sounder with VAD and isolator |  | 0.00158 | 0 | 0 | 0.03345 | 0
MAD-565-I (External PS) | Addressable sounder with VAD and isolator |  | 0.00035 | 0 | 0 | 0.0008 | 0
MAD-565-I - only flash (loop) | Addressable VAD with isolator |  | 0.00158 | 0 | 0 | 0.03345 | 0
MAD-565-I - only flash (External PS) | Addressable VAD with isolator |  | 0.00035 | 0 | 0 | 0.0008 | 0
MAD-567-I (loop) | Sounder base with isolator |  | 0.00117 | 0 | 0 | 0.00895 | 0
MAD-567-I (External PS) | Sounder base with isolator |  | 0.000261 | 0 | 0 | 0.00071 | 0
MAD-569-I (loop) | Sounder & VAD base with isolator |  | 0.00117 | 0 | 0 | 0.02326 | 0
MAD-569-I (External PS) | Sounder & VAD base with isolator |  | 0.0002589 | 0 | 0 | 0.00071 | 0
MAD-569-I - only flash (loop) | VAD base with isolator |  | 0.00117 | 0 | 0 | 0.02326 | 0
MAD-569-I only flash (External PS) | VAD base with isolator |  | 0.0002589 | 0 | 0 | 0.00071 | 0
MAD-472 | Sounder base |  | 0.0001074 | 0 | 0 | 0.00845 | 0
MAD-473 | Sounder base with flash |  | 0.0001068 | 0 | 0 | 0.00948 | 0
MAD-481 | 1 output 230V addressable module |  | 0.0003 | 0 | 0 | 0.003 | 0
MAD-481-I | 1 output 230V addressable module with isolator |  | 0.0003 | 0 | 0 | 0.003 | 0
MAD-490 | Isolator module |  | 6.96e-05 | 0 | 0 | 0.03766 | 0
PAD-10A-I | Remote indicator with isolator |  | 0.0001764 | 0 | 0 | 0.00298 | 0
TPLD-100 (CCD-102) = 3 loop address | 2 zones fire alarm control panel connected to loop |  | 0.001863 | 0 | 0 | 0.00186 | 0
TPLD-100 (CCD-104) = 5 loop address | 4 zones fire alarm control panel connected to loop |  | 0.001863 | 0 | 0 | 0.00186 | 0
TPLD-100 (CCD-108) = 9 loop address | 8 zones fire alarm control panel connected to loop |  | 0.001863 | 0 | 0 | 0.00186 | 0
TPLD-100 (CCD-112) = 13 loop address | 12 zones fire alarm control panel connected to loop |  | 0.001863 | 0 | 0 | 0.00186 | 0
TPLD-100 (CCD-103) = 7 loop address | Extinguishing control panel connected to loop |  | 0.001863 | 0 | 0 | 0.00186 | 0
Total |  | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
Loop Parameters
Cu | 0.0172 | Ω*mm2/m
I_Standby | 0 | A
I_Alarm | 0 | A
I_Sounders | 0 | A
I_Total | 0 | A
V_Lin_Ring | 6.9 | V
Minimum Cable Section for common Lenghts | [10 empty] | Warning: The Minimum Cable Seccion in the Loop is 0,5 mm2
Lenghts | 1000 | 1500 |  | 2000 |  |  | 2500 | 3000 | 3500 | m
R_Cable | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! | #DIV/0! | Ω
R_eq_Ring | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! | #DIV/0! | Ω
S_min | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | mm2
Maximum Cable Lenght for Standard Cable Section (IEC 60228) | [10 empty] | Warning: The Maximum Cable Length in the Loop is 3500 meters
Section | 0.5 | 0.75 |  | 1 |  |  | 1.5 | 2.5 | 4 | mm2
R_Cable | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! | #DIV/0! | Ω
R_eq_Ring | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! | #DIV/0! | Ω
L_max | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | m
Maximum Current Calculation
? S | 1.5 | mm2
? L | 1000 | mm2
R_Cable_Sys | 22.9333 | Ω
R_eq_Ring_Sys | 11.4667 | Ω
I_max | 0.60174 | A
System Check
Current |  | OK
Addresses |  | OK
This tool may be used as a design help for Detnov Security S.L. We reserve the right not to be responsible for its accuracy, completeness or quality of the information provided, including any kind of information which could be incomplete or incorrect.

## SC_Loop 2
SYSTEM CALCULATOR DETNOV CAD-150 EXCEL TOOL | [11 empty] | SC 116 en 2019 i
Loop | [9 empty] | System Check
Section of wire | 1.5 | 16 | [7 empty] | Current |  | OK
Lenght loop | 1000 | meters | [7 empty] | Addresses |  | OK
Fill Cable Section in mm2 and the Line Distance in meters (Yelow field)
|  | Fill the PCS field for the desired configuration (Yelow field) | Fill the PCS field for the desired configuration (Yelow field)
Devices Loop 2
REF. | Description | PCS | I_Standby (A) | I_Standby (A) | PCS_alarm | I_Alarm (A) | I_Alarm (A) | I_Sounders (A) | DET | MOD | SND | ADR
DOD-220A | Addressable smoke detector |  | 0.0001272 | 0 | 0 | 0.00361 | 0
DOD-220A-I | Addressable smoke detector with isolator |  | 0.0001958 | 0 | 0 | 0.00374 | 0
DOTD-230A | Addressable smoke and heat detector |  | 0.0001416 | 0 | 0 | 0.0036 | 0
DOTD-230A-I | Addressable smoke and heat detector with isolator |  | 0.0002124 | 0 | 0 | 0.00374 | 0
DTD-210A | Addressable heat detector |  | 0.0001222 | 0 | 0 | 0.00364 | 0
DTD-210A-I | Addressable heat detector with isolator |  | 0.0001924 | 0 | 0 | 0.00376 | 0
DTD-215A | Addressable high temperature detector |  | 0.0001337 | 0 | 0 | 0.00378 | 0
DTD-215A-I | Addressable high temperature detector with isolator |  | 0.0002035 | 0 | 0 | 0.00377 | 0
DGD-600 | Stand-alone natural gas detector (24V) |  | 0.00218 | 0 | 0 | 0.00222 | 0
DGD-600-AC | Stand-alone natural gas detector (230V) |  | 0.0026 | 0 | 0 | 0.00316 | 0
DGD-620 | Stand-alone LPG detector (24V) |  | 0.00218 | 0 | 0 | 0.00222 | 0
DGD-620-AC | Stand-alone LPG detector (230V) |  | 0.0026 | 0 | 0 | 0.00316 | 0
DBD-70A | Addressable lineal smoke detector |  | 0.038 | 0 | 0 | 0.038 | 0
MAD-401 & MAD-401-I | 1 output addressable module |  | 0.0002168 | 0 | 0 | 0.00306 | 0
MAD-402 & MAD-402-I | 2 outputs addressable module |  | 0.0002174 | 0 | 0 | 0.00595 | 0 |  |  | 0
MAD-405-I | 5 outputs addressable module |  | 0.0002786 | 0 | 0 | 0.00315 | 0 |  |  | 0
MAD-409-I | 10 outputs addressable module |  | 0.0003677 | 0 | 0 | 0.0033 | 0
MAD-411 & MAD-411-I | 1 input addressable module |  | 0.0001916 | 0 | 0 | 0.00306 | 0
MAD-412 & MAD-412-I | 2 inputs addressable module |  | 0.000191 | 0 | 0 | 0.00584 | 0 |  |  | 0
MAD-415-I | 5 inputs addressable module |  | 0.0001888 | 0 | 0 | 0.00395 | 0 |  |  | 0
MAD-419-I | 10 inputs addressable module |  | 0.0001892 | 0 | 0 | 0.00484 | 0 |  |  | 0
MAD-421 & MAD-421-I | 1 output/1 input addressable module |  | 0.0002101 | 0 | 0 | 0.00592 | 0 |  |  | 0
MAD-422 & MAD-422-I | 2 outputs/2 inputs addressable module |  | 0.000234 | 0 | 0 | 0.00591 | 0 |  |  | 0
MAD-425-I | 5 outputs/5 inputs addressable module |  | 0.000284 | 0 | 0 | 0.00408 | 0 |  |  | 0
MAD-429-I | 10 outputs/10 inputs addressable module |  | 0.0003766 | 0 | 0 | 0.005 | 0 |  |  | 0
MAD-431 & MAD-431-I | 1 output 24V addressable module |  | 0.000215 | 0 | 0 | 0.00361 | 0
MAD-432 & MAD-432-I | 2 outputs 24V addressable module |  | 0.0002033 | 0 | 0 | 0.0068 | 0
MAD-441 & MAD-441-I | 1 conventional zone addressable module |  | 0.0001878 | 0 | 0 | 0.00304 | 0
MAD-442 & MAD-442-I | 2 conventionals zones addressable module |  | 0.0001878 | 0 | 0 | 0.00584 | 0
MAD-450 & MAD-450-I | Addressable manual call point with isolator |  | 0.0001766 | 0 | 0 | 0.00303 | 0
MAD-451-I | Addressable manual call point with isolator |  | 0.0001774 | 0 | 0 | 0.003 | 0
MAD-461-I | Addressable sounder with isolator |  | 0.0001769 | 0 | 0 | 0.00835 | 0
MAD-464-I Low Volume (78 dB) | Addressable sounder with isolator |  | 0.0001765 | 0 | 0 | 0.01232 | 0
MAD-464-I Medium Volume (93 dB) | Addressable sounder with isolator |  | 0.0001765 | 0 | 0 | 0.01232 | 0
MAD-464-I High Volume (97 dB) | Addressable sounder with isolator |  | 0.0001765 | 0 | 0 | 0.01232 | 0
MAD-465-I Low Volume (78 dB) | Addressable sounder with beacon and isolator |  | 0.0001773 | 0 | 0 | 0.01232 | 0
MAD-465-I Medium Volume (93 dB) | Addressable sounder with beacon and isolator |  | 0.0001773 | 0 | 0 | 0.01232 | 0
MAD-465-I High Volume (97 dB) | Addressable sounder with beacon and isolator |  | 0.0001773 | 0 | 0 | 0.01232 | 0
MAD-564-I (loop) | Addressable sounder with isolator |  | 0.00158 | 0 | 0 | 0.02111 | 0
MAD-564-I (External PS) | Addressable sounder with isolator |  | 0.00035 | 0 | 0 | 0.0008 | 0
MAD-565-I (loop) | Addressable sounder with VAD and isolator |  | 0.00158 | 0 | 0 | 0.03345 | 0
MAD-565-I (External PS) | Addressable sounder with VAD and isolator |  | 0.00035 | 0 | 0 | 0.0008 | 0
MAD-565-I - only flash (loop) | Addressable VAD with isolator |  | 0.00158 | 0 | 0 | 0.03345 | 0
MAD-565-I - only flash (External PS) | Addressable VAD with isolator |  | 0.00035 | 0 | 0 | 0.0008 | 0
MAD-567-I (loop) | Sounder base with isolator |  | 0.00117 | 0 | 0 | 0.00895 | 0
MAD-567-I (External PS) | Sounder base with isolator |  | 0.000261 | 0 | 0 | 0.00071 | 0
MAD-569-I (loop) | Sounder & VAD base with isolator |  | 0.00117 | 0 | 0 | 0.02326 | 0
MAD-569-I (External PS) | Sounder & VAD base with isolator |  | 0.0002589 | 0 | 0 | 0.00071 | 0
MAD-569-I - only flash (loop) | VAD base with isolator |  | 0.00117 | 0 | 0 | 0.02326 | 0
MAD-569-I only flash (External PS) | VAD base with isolator |  | 0.0002589 | 0 | 0 | 0.00071 | 0
MAD-472 | Sounder base |  | 0.0001074 | 0 | 0 | 0.00845 | 0
MAD-473 | Sounder base with flash |  | 0.0001068 | 0 | 0 | 0.00948 | 0
MAD-481 | 1 output 230V addressable module |  | 0.0003 | 0 | 0 | 0.003 | 0
MAD-481-I | 1 output 230V addressable module with isolator |  | 0.0003 | 0 | 0 | 0.003 | 0
MAD-490 | Isolator module |  | 6.96e-05 | 0 | 0 | 0.03766 | 0
PAD-10A-I | Remote indicator with isolator |  | 0.0001764 | 0 | 0 | 0.00298 | 0
TPLD-100 (CCD-102) = 3 loop address | 2 zones fire alarm control panel connected to loop |  | 0.001863 | 0 | 0 | 0.00186 | 0
TPLD-100 (CCD-104) = 5 loop address | 4 zones fire alarm control panel connected to loop |  | 0.001863 | 0 | 0 | 0.00186 | 0
TPLD-100 (CCD-108) = 9 loop address | 8 zones fire alarm control panel connected to loop |  | 0.001863 | 0 | 0 | 0.00186 | 0
TPLD-100 (CCD-112) = 13 loop address | 12 zones fire alarm control panel connected to loop |  | 0.001863 | 0 | 0 | 0.00186 | 0
TPLD-100 (CCD-103) = 7 loop address | Extinguishing control panel connected to loop |  | 0.001863 | 0 | 0 | 0.00186 | 0
Total |  | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
Loop Parameters
Cu | 0.0172 | Ω*mm2/m
I_Standby | 0 | A
I_Alarm | 0 | A
I_Sounders | 0 | A
I_Total | 0 | A
V_Lin_Ring | 6.9 | V
Minimum Cable Section for common Lenghts | [10 empty] | Warning: The Minimum Cable Seccion in the Loop is 0,5 mm2
Lenghts | 1000 | 1500 |  | 2000 |  |  | 2500 | 3000 | 3500 | m
R_Cable | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! | #DIV/0! | Ω
R_eq_Ring | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! | #DIV/0! | Ω
S_min | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | mm2
Maximum Cable Lenght for Standard Cable Section (IEC 60228) | [10 empty] | Warning: The Maximum Cable Length in the Loop is 3500 meters
Section | 0.5 | 0.75 |  | 1 |  |  | 1.5 | 2.5 | 4 | mm2
R_Cable | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! | #DIV/0! | Ω
R_eq_Ring | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! | #DIV/0! | Ω
L_max | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | m
Maximum Current Calculation
? S | 1.5 | mm2
? L | 1000 | mm2
R_Cable_Sys | 22.9333 | Ω
R_eq_Ring_Sys | 11.4667 | Ω
I_max | 0.60174 | A
System Check
Current |  | OK
Addresses |  | OK
This tool may be used as a design help for Detnov Security S.L. We reserve the right not to be responsible for its accuracy, completeness or quality of the information provided, including any kind of information which could be incomplete or incorrect.

## SC_Loop 3
SYSTEM CALCULATOR DETNOV CAD-150 EXCEL TOOL | [11 empty] | SC 116 en 2019 i
Loop | [9 empty] | System Check
Section of wire | 1.5 | 16 | [7 empty] | Current |  | OK
Lenght loop | 1000 | meters | [7 empty] | Addresses |  | OK
Fill Cable Section in mm2 and the Line Distance in meters (Yelow field)
|  | Fill the PCS field for the desired configuration (Yelow field) | Fill the PCS field for the desired configuration (Yelow field)
Devices Loop 3
REF. | Description | PCS | I_Standby (A) | I_Standby (A) | PCS_alarm | I_Alarm (A) | I_Alarm (A) | I_Sounders (A) | DET | MOD | SND | ADR
DOD-220A | Addressable smoke detector |  | 0.0001272 | 0 | 0 | 0.00361 | 0
DOD-220A-I | Addressable smoke detector with isolator |  | 0.0001958 | 0 | 0 | 0.00374 | 0
DOTD-230A | Addressable smoke and heat detector |  | 0.0001416 | 0 | 0 | 0.0036 | 0
DOTD-230A-I | Addressable smoke and heat detector with isolator |  | 0.0002124 | 0 | 0 | 0.00374 | 0
DTD-210A | Addressable heat detector |  | 0.0001222 | 0 | 0 | 0.00364 | 0
DTD-210A-I | Addressable heat detector with isolator |  | 0.0001924 | 0 | 0 | 0.00376 | 0
DTD-215A | Addressable high temperature detector |  | 0.0001337 | 0 | 0 | 0.00378 | 0
DTD-215A-I | Addressable high temperature detector with isolator |  | 0.0002035 | 0 | 0 | 0.00377 | 0
DGD-600 | Stand-alone natural gas detector (24V) |  | 0.00218 | 0 | 0 | 0.00222 | 0
DGD-600-AC | Stand-alone natural gas detector (230V) |  | 0.0026 | 0 | 0 | 0.00316 | 0
DGD-620 | Stand-alone LPG detector (24V) |  | 0.00218 | 0 | 0 | 0.00222 | 0
DGD-620-AC | Stand-alone LPG detector (230V) |  | 0.0026 | 0 | 0 | 0.00316 | 0
DBD-70A | Addressable lineal smoke detector |  | 0.038 | 0 | 0 | 0.038 | 0
MAD-401 & MAD-401-I | 1 output addressable module |  | 0.0002168 | 0 | 0 | 0.00306 | 0
MAD-402 & MAD-402-I | 2 outputs addressable module |  | 0.0002174 | 0 | 0 | 0.00595 | 0 |  |  | 0
MAD-405-I | 5 outputs addressable module |  | 0.0002786 | 0 | 0 | 0.00315 | 0 |  |  | 0
MAD-409-I | 10 outputs addressable module |  | 0.0003677 | 0 | 0 | 0.0033 | 0
MAD-411 & MAD-411-I | 1 input addressable module |  | 0.0001916 | 0 | 0 | 0.00306 | 0
MAD-412 & MAD-412-I | 2 inputs addressable module |  | 0.000191 | 0 | 0 | 0.00584 | 0 |  |  | 0
MAD-415-I | 5 inputs addressable module |  | 0.0001888 | 0 | 0 | 0.00395 | 0 |  |  | 0
MAD-419-I | 10 inputs addressable module |  | 0.0001892 | 0 | 0 | 0.00484 | 0 |  |  | 0
MAD-421 & MAD-421-I | 1 output/1 input addressable module |  | 0.0002101 | 0 | 0 | 0.00592 | 0 |  |  | 0
MAD-422 & MAD-422-I | 2 outputs/2 inputs addressable module |  | 0.000234 | 0 | 0 | 0.00591 | 0 |  |  | 0
MAD-425-I | 5 outputs/5 inputs addressable module |  | 0.000284 | 0 | 0 | 0.00408 | 0 |  |  | 0
MAD-429-I | 10 outputs/10 inputs addressable module |  | 0.0003766 | 0 | 0 | 0.005 | 0 |  |  | 0
MAD-431 & MAD-431-I | 1 output 24V addressable module |  | 0.000215 | 0 | 0 | 0.00361 | 0
MAD-432 & MAD-432-I | 2 outputs 24V addressable module |  | 0.0002033 | 0 | 0 | 0.0068 | 0
MAD-441 & MAD-441-I | 1 conventional zone addressable module |  | 0.0001878 | 0 | 0 | 0.00304 | 0
MAD-442 & MAD-442-I | 2 conventionals zones addressable module |  | 0.0001878 | 0 | 0 | 0.00584 | 0
MAD-450 & MAD-450-I | Addressable manual call point with isolator |  | 0.0001766 | 0 | 0 | 0.00303 | 0
MAD-451-I | Addressable manual call point with isolator |  | 0.0001774 | 0 | 0 | 0.003 | 0
MAD-461-I | Addressable sounder with isolator |  | 0.0001769 | 0 | 0 | 0.00835 | 0
MAD-464-I Low Volume (78 dB) | Addressable sounder with isolator |  | 0.0001765 | 0 | 0 | 0.01232 | 0
MAD-464-I Medium Volume (93 dB) | Addressable sounder with isolator |  | 0.0001765 | 0 | 0 | 0.01232 | 0
MAD-464-I High Volume (97 dB) | Addressable sounder with isolator |  | 0.0001765 | 0 | 0 | 0.01232 | 0
MAD-465-I Low Volume (78 dB) | Addressable sounder with beacon and isolator |  | 0.0001773 | 0 | 0 | 0.01232 | 0
MAD-465-I Medium Volume (93 dB) | Addressable sounder with beacon and isolator |  | 0.0001773 | 0 | 0 | 0.01232 | 0
MAD-465-I High Volume (97 dB) | Addressable sounder with beacon and isolator |  | 0.0001773 | 0 | 0 | 0.01232 | 0
MAD-564-I (loop) | Addressable sounder with isolator |  | 0.00158 | 0 | 0 | 0.02111 | 0
MAD-564-I (External PS) | Addressable sounder with isolator |  | 0.00035 | 0 | 0 | 0.0008 | 0
MAD-565-I (loop) | Addressable sounder with VAD and isolator |  | 0.00158 | 0 | 0 | 0.03345 | 0
MAD-565-I (External PS) | Addressable sounder with VAD and isolator |  | 0.00035 | 0 | 0 | 0.0008 | 0
MAD-565-I - only flash (loop) | Addressable VAD with isolator |  | 0.00158 | 0 | 0 | 0.03345 | 0
MAD-565-I - only flash (External PS) | Addressable VAD with isolator |  | 0.00035 | 0 | 0 | 0.0008 | 0
MAD-567-I (loop) | Sounder base with isolator |  | 0.00117 | 0 | 0 | 0.00895 | 0
MAD-567-I (External PS) | Sounder base with isolator |  | 0.000261 | 0 | 0 | 0.00071 | 0
MAD-569-I (loop) | Sounder & VAD base with isolator |  | 0.00117 | 0 | 0 | 0.02326 | 0
MAD-569-I (External PS) | Sounder & VAD base with isolator |  | 0.0002589 | 0 | 0 | 0.00071 | 0
MAD-569-I - only flash (loop) | VAD base with isolator |  | 0.00117 | 0 | 0 | 0.02326 | 0
MAD-569-I only flash (External PS) | VAD base with isolator |  | 0.0002589 | 0 | 0 | 0.00071 | 0
MAD-472 | Sounder base |  | 0.0001074 | 0 | 0 | 0.00845 | 0
MAD-473 | Sounder base with flash |  | 0.0001068 | 0 | 0 | 0.00948 | 0
MAD-481 | 1 output 230V addressable module |  | 0.0003 | 0 | 0 | 0.003 | 0
MAD-481-I | 1 output 230V addressable module with isolator |  | 0.0003 | 0 | 0 | 0.003 | 0
MAD-490 | Isolator module |  | 6.96e-05 | 0 | 0 | 0.03766 | 0
PAD-10A-I | Remote indicator with isolator |  | 0.0001764 | 0 | 0 | 0.00298 | 0
TPLD-100 (CCD-102) = 3 loop address | 2 zones fire alarm control panel connected to loop |  | 0.001863 | 0 | 0 | 0.00186 | 0
TPLD-100 (CCD-104) = 5 loop address | 4 zones fire alarm control panel connected to loop |  | 0.001863 | 0 | 0 | 0.00186 | 0
TPLD-100 (CCD-108) = 9 loop address | 8 zones fire alarm control panel connected to loop |  | 0.001863 | 0 | 0 | 0.00186 | 0
TPLD-100 (CCD-112) = 13 loop address | 12 zones fire alarm control panel connected to loop |  | 0.001863 | 0 | 0 | 0.00186 | 0
TPLD-100 (CCD-103) = 7 loop address | Extinguishing control panel connected to loop |  | 0.001863 | 0 | 0 | 0.00186 | 0
Total |  | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
Loop Parameters
Cu | 0.0172 | Ω*mm2/m
I_Standby | 0 | A
I_Alarm | 0 | A
I_Sounders | 0 | A
I_Total | 0 | A
V_Lin_Ring | 6.9 | V
Minimum Cable Section for common Lenghts | [10 empty] | Warning: The Minimum Cable Seccion in the Loop is 0,5 mm2
Lenghts | 1000 | 1500 |  | 2000 |  |  | 2500 | 3000 | 3500 | m
R_Cable | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! | #DIV/0! | Ω
R_eq_Ring | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! | #DIV/0! | Ω
S_min | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | mm2
Maximum Cable Lenght for Standard Cable Section (IEC 60228) | [10 empty] | Warning: The Maximum Cable Length in the Loop is 3500 meters
Section | 0.5 | 0.75 |  | 1 |  |  | 1.5 | 2.5 | 4 | mm2
R_Cable | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! | #DIV/0! | Ω
R_eq_Ring | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! | #DIV/0! | Ω
L_max | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | m
Maximum Current Calculation
? S | 1.5 | mm2
? L | 1000 | mm2
R_Cable_Sys | 22.9333 | Ω
R_eq_Ring_Sys | 11.4667 | Ω
I_max | 0.60174 | A
System Check
Current |  | OK
Addresses |  | OK
This tool may be used as a design help for Detnov Security S.L. We reserve the right not to be responsible for its accuracy, completeness or quality of the information provided, including any kind of information which could be incomplete or incorrect.

## SC_Loop 4
SYSTEM CALCULATOR DETNOV CAD-150 EXCEL TOOL | [11 empty] | SC 116 en 2019 i
Loop | [9 empty] | System Check
Section of wire | 1.5 | 16 | [7 empty] | Current |  | OK
Lenght loop | 1000 | meters | [7 empty] | Addresses |  | OK
Fill Cable Section in mm2 and the Line Distance in meters (Yelow field)
|  | Fill the PCS field for the desired configuration (Yelow field) | Fill the PCS field for the desired configuration (Yelow field)
Devices Loop 4
REF. | Description | PCS | I_Standby (A) | I_Standby (A) | PCS_alarm | I_Alarm (A) | I_Alarm (A) | I_Sounders (A) | DET | MOD | SND | ADR
DOD-220A | Addressable smoke detector |  | 0.0001272 | 0 | 0 | 0.00361 | 0
DOD-220A-I | Addressable smoke detector with isolator |  | 0.0001958 | 0 | 0 | 0.00374 | 0
DOTD-230A | Addressable smoke and heat detector |  | 0.0001416 | 0 | 0 | 0.0036 | 0
DOTD-230A-I | Addressable smoke and heat detector with isolator |  | 0.0002124 | 0 | 0 | 0.00374 | 0
DTD-210A | Addressable heat detector |  | 0.0001222 | 0 | 0 | 0.00364 | 0
DTD-210A-I | Addressable heat detector with isolator |  | 0.0001924 | 0 | 0 | 0.00376 | 0
DTD-215A | Addressable high temperature detector |  | 0.0001337 | 0 | 0 | 0.00378 | 0
DTD-215A-I | Addressable high temperature detector with isolator |  | 0.0002035 | 0 | 0 | 0.00377 | 0
DGD-600 | Stand-alone natural gas detector (24V) |  | 0.00218 | 0 | 0 | 0.00222 | 0
DGD-600-AC | Stand-alone natural gas detector (230V) |  | 0.0026 | 0 | 0 | 0.00316 | 0
DGD-620 | Stand-alone LPG detector (24V) |  | 0.00218 | 0 | 0 | 0.00222 | 0
DGD-620-AC | Stand-alone LPG detector (230V) |  | 0.0026 | 0 | 0 | 0.00316 | 0
DBD-70A | Addressable lineal smoke detector |  | 0.038 | 0 | 0 | 0.038 | 0
MAD-401 & MAD-401-I | 1 output addressable module |  | 0.0002168 | 0 | 0 | 0.00306 | 0
MAD-402 & MAD-402-I | 2 outputs addressable module |  | 0.0002174 | 0 | 0 | 0.00595 | 0 |  |  | 0
MAD-405-I | 5 outputs addressable module |  | 0.0002786 | 0 | 0 | 0.00315 | 0 |  |  | 0
MAD-409-I | 10 outputs addressable module |  | 0.0003677 | 0 | 0 | 0.0033 | 0
MAD-411 & MAD-411-I | 1 input addressable module |  | 0.0001916 | 0 | 0 | 0.00306 | 0
MAD-412 & MAD-412-I | 2 inputs addressable module |  | 0.000191 | 0 | 0 | 0.00584 | 0 |  |  | 0
MAD-415-I | 5 inputs addressable module |  | 0.0001888 | 0 | 0 | 0.00395 | 0 |  |  | 0
MAD-419-I | 10 inputs addressable module |  | 0.0001892 | 0 | 0 | 0.00484 | 0 |  |  | 0
MAD-421 & MAD-421-I | 1 output/1 input addressable module |  | 0.0002101 | 0 | 0 | 0.00592 | 0 |  |  | 0
MAD-422 & MAD-422-I | 2 outputs/2 inputs addressable module |  | 0.000234 | 0 | 0 | 0.00591 | 0 |  |  | 0
MAD-425-I | 5 outputs/5 inputs addressable module |  | 0.000284 | 0 | 0 | 0.00408 | 0 |  |  | 0
MAD-429-I | 10 outputs/10 inputs addressable module |  | 0.0003766 | 0 | 0 | 0.005 | 0 |  |  | 0
MAD-431 & MAD-431-I | 1 output 24V addressable module |  | 0.000215 | 0 | 0 | 0.00361 | 0
MAD-432 & MAD-432-I | 2 outputs 24V addressable module |  | 0.0002033 | 0 | 0 | 0.0068 | 0
MAD-441 & MAD-441-I | 1 conventional zone addressable module |  | 0.0001878 | 0 | 0 | 0.00304 | 0
MAD-442 & MAD-442-I | 2 conventionals zones addressable module |  | 0.0001878 | 0 | 0 | 0.00584 | 0
MAD-450 & MAD-450-I | Addressable manual call point with isolator |  | 0.0001766 | 0 | 0 | 0.00303 | 0
MAD-451-I | Addressable manual call point with isolator |  | 0.0001774 | 0 | 0 | 0.003 | 0
MAD-461-I | Addressable sounder with isolator |  | 0.0001769 | 0 | 0 | 0.00835 | 0
MAD-464-I Low Volume (78 dB) | Addressable sounder with isolator |  | 0.0001765 | 0 | 0 | 0.01232 | 0
MAD-464-I Medium Volume (93 dB) | Addressable sounder with isolator |  | 0.0001765 | 0 | 0 | 0.01232 | 0
MAD-464-I High Volume (97 dB) | Addressable sounder with isolator |  | 0.0001765 | 0 | 0 | 0.01232 | 0
MAD-465-I Low Volume (78 dB) | Addressable sounder with beacon and isolator |  | 0.0001773 | 0 | 0 | 0.01232 | 0
MAD-465-I Medium Volume (93 dB) | Addressable sounder with beacon and isolator |  | 0.0001773 | 0 | 0 | 0.01232 | 0
MAD-465-I High Volume (97 dB) | Addressable sounder with beacon and isolator |  | 0.0001773 | 0 | 0 | 0.01232 | 0
MAD-564-I (loop) | Addressable sounder with isolator |  | 0.00158 | 0 | 0 | 0.02111 | 0
MAD-564-I (External PS) | Addressable sounder with isolator |  | 0.00035 | 0 | 0 | 0.0008 | 0
MAD-565-I (loop) | Addressable sounder with VAD and isolator |  | 0.00158 | 0 | 0 | 0.03345 | 0
MAD-565-I (External PS) | Addressable sounder with VAD and isolator |  | 0.00035 | 0 | 0 | 0.0008 | 0
MAD-565-I - only flash (loop) | Addressable VAD with isolator |  | 0.00158 | 0 | 0 | 0.03345 | 0
MAD-565-I - only flash (External PS) | Addressable VAD with isolator |  | 0.00035 | 0 | 0 | 0.0008 | 0
MAD-567-I (loop) | Sounder base with isolator |  | 0.00117 | 0 | 0 | 0.00895 | 0
MAD-567-I (External PS) | Sounder base with isolator |  | 0.000261 | 0 | 0 | 0.00071 | 0
MAD-569-I (loop) | Sounder & VAD base with isolator |  | 0.00117 | 0 | 0 | 0.02326 | 0
MAD-569-I (External PS) | Sounder & VAD base with isolator |  | 0.0002589 | 0 | 0 | 0.00071 | 0
MAD-569-I - only flash (loop) | VAD base with isolator |  | 0.00117 | 0 | 0 | 0.02326 | 0
MAD-569-I only flash (External PS) | VAD base with isolator |  | 0.0002589 | 0 | 0 | 0.00071 | 0
MAD-472 | Sounder base |  | 0.0001074 | 0 | 0 | 0.00845 | 0
MAD-473 | Sounder base with flash |  | 0.0001068 | 0 | 0 | 0.00948 | 0
MAD-481 | 1 output 230V addressable module |  | 0.0003 | 0 | 0 | 0.003 | 0
MAD-481-I | 1 output 230V addressable module with isolator |  | 0.0003 | 0 | 0 | 0.003 | 0
MAD-490 | Isolator module |  | 6.96e-05 | 0 | 0 | 0.03766 | 0
PAD-10A-I | Remote indicator with isolator |  | 0.0001764 | 0 | 0 | 0.00298 | 0
TPLD-100 (CCD-102) = 3 loop address | 2 zones fire alarm control panel connected to loop |  | 0.001863 | 0 | 0 | 0.00186 | 0
TPLD-100 (CCD-104) = 5 loop address | 4 zones fire alarm control panel connected to loop |  | 0.001863 | 0 | 0 | 0.00186 | 0
TPLD-100 (CCD-108) = 9 loop address | 8 zones fire alarm control panel connected to loop |  | 0.001863 | 0 | 0 | 0.00186 | 0
TPLD-100 (CCD-112) = 13 loop address | 12 zones fire alarm control panel connected to loop |  | 0.001863 | 0 | 0 | 0.00186 | 0
TPLD-100 (CCD-103) = 7 loop address | Extinguishing control panel connected to loop |  | 0.001863 | 0 | 0 | 0.00186 | 0
Total |  | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
Loop Parameters
Cu | 0.0172 | Ω*mm2/m
I_Standby | 0 | A
I_Alarm | 0 | A
I_Sounders | 0 | A
I_Total | 0 | A
V_Lin_Ring | 6.9 | V
Minimum Cable Section for common Lenghts | [10 empty] | Warning: The Minimum Cable Seccion in the Loop is 0,5 mm2
Lenghts | 1000 | 1500 |  | 2000 |  |  | 2500 | 3000 | 3500 | m
R_Cable | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! | #DIV/0! | Ω
R_eq_Ring | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! | #DIV/0! | Ω
S_min | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | mm2
Maximum Cable Lenght for Standard Cable Section (IEC 60228) | [10 empty] | Warning: The Maximum Cable Length in the Loop is 3500 meters
Section | 0.5 | 0.75 |  | 1 |  |  | 1.5 | 2.5 | 4 | mm2
R_Cable | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! | #DIV/0! | Ω
R_eq_Ring | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! | #DIV/0! | Ω
L_max | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | m
Maximum Current Calculation
? S | 1.5 | mm2
? L | 1000 | mm2
R_Cable_Sys | 22.9333 | Ω
R_eq_Ring_Sys | 11.4667 | Ω
I_max | 0.60174 | A
System Check
Current |  | OK
Addresses |  | OK
This tool may be used as a design help for Detnov Security S.L. We reserve the right not to be responsible for its accuracy, completeness or quality of the information provided, including any kind of information which could be incomplete or incorrect.

## SC_Loop 5
SYSTEM CALCULATOR DETNOV CAD-150 EXCEL TOOL | [11 empty] | SC 116 en 2019 i
Loop | [9 empty] | System Check
Section of wire | 1.5 | 16 | [7 empty] | Current |  | OK
Lenght loop | 1000 | meters | [7 empty] | Addresses |  | OK
Fill Cable Section in mm2 and the Line Distance in meters (Yelow field)
|  | Fill the PCS field for the desired configuration (Yelow field) | Fill the PCS field for the desired configuration (Yelow field)
Devices Loop 5
REF. | Description | PCS | I_Standby (A) | I_Standby (A) | PCS_alarm | I_Alarm (A) | I_Alarm (A) | I_Sounders (A) | DET | MOD | SND | ADR
DOD-220A | Addressable smoke detector |  | 0.0001272 | 0 | 0 | 0.00361 | 0
DOD-220A-I | Addressable smoke detector with isolator |  | 0.0001958 | 0 | 0 | 0.00374 | 0
DOTD-230A | Addressable smoke and heat detector |  | 0.0001416 | 0 | 0 | 0.0036 | 0
DOTD-230A-I | Addressable smoke and heat detector with isolator |  | 0.0002124 | 0 | 0 | 0.00374 | 0
DTD-210A | Addressable heat detector |  | 0.0001222 | 0 | 0 | 0.00364 | 0
DTD-210A-I | Addressable heat detector with isolator |  | 0.0001924 | 0 | 0 | 0.00376 | 0
DTD-215A | Addressable high temperature detector |  | 0.0001337 | 0 | 0 | 0.00378 | 0
DTD-215A-I | Addressable high temperature detector with isolator |  | 0.0002035 | 0 | 0 | 0.00377 | 0
DGD-600 | Stand-alone natural gas detector (24V) |  | 0.00218 | 0 | 0 | 0.00222 | 0
DGD-600-AC | Stand-alone natural gas detector (230V) |  | 0.0026 | 0 | 0 | 0.00316 | 0
DGD-620 | Stand-alone LPG detector (24V) |  | 0.00218 | 0 | 0 | 0.00222 | 0
DGD-620-AC | Stand-alone LPG detector (230V) |  | 0.0026 | 0 | 0 | 0.00316 | 0
DBD-70A | Addressable lineal smoke detector |  | 0.038 | 0 | 0 | 0.038 | 0
MAD-401 & MAD-401-I | 1 output addressable module |  | 0.0002168 | 0 | 0 | 0.00306 | 0
MAD-402 & MAD-402-I | 2 outputs addressable module |  | 0.0002174 | 0 | 0 | 0.00595 | 0 |  |  | 0
MAD-405-I | 5 outputs addressable module |  | 0.0002786 | 0 | 0 | 0.00315 | 0 |  |  | 0
MAD-409-I | 10 outputs addressable module |  | 0.0003677 | 0 | 0 | 0.0033 | 0
MAD-411 & MAD-411-I | 1 input addressable module |  | 0.0001916 | 0 | 0 | 0.00306 | 0
MAD-412 & MAD-412-I | 2 inputs addressable module |  | 0.000191 | 0 | 0 | 0.00584 | 0 |  |  | 0
MAD-415-I | 5 inputs addressable module |  | 0.0001888 | 0 | 0 | 0.00395 | 0 |  |  | 0
MAD-419-I | 10 inputs addressable module |  | 0.0001892 | 0 | 0 | 0.00484 | 0 |  |  | 0
MAD-421 & MAD-421-I | 1 output/1 input addressable module |  | 0.0002101 | 0 | 0 | 0.00592 | 0 |  |  | 0
MAD-422 & MAD-422-I | 2 outputs/2 inputs addressable module |  | 0.000234 | 0 | 0 | 0.00591 | 0 |  |  | 0
MAD-425-I | 5 outputs/5 inputs addressable module |  | 0.000284 | 0 | 0 | 0.00408 | 0 |  |  | 0
MAD-429-I | 10 outputs/10 inputs addressable module |  | 0.0003766 | 0 | 0 | 0.005 | 0 |  |  | 0
MAD-431 & MAD-431-I | 1 output 24V addressable module |  | 0.000215 | 0 | 0 | 0.00361 | 0
MAD-432 & MAD-432-I | 2 outputs 24V addressable module |  | 0.0002033 | 0 | 0 | 0.0068 | 0
MAD-441 & MAD-441-I | 1 conventional zone addressable module |  | 0.0001878 | 0 | 0 | 0.00304 | 0
MAD-442 & MAD-442-I | 2 conventionals zones addressable module |  | 0.0001878 | 0 | 0 | 0.00584 | 0
MAD-450 & MAD-450-I | Addressable manual call point with isolator |  | 0.0001766 | 0 | 0 | 0.00303 | 0
MAD-451-I | Addressable manual call point with isolator |  | 0.0001774 | 0 | 0 | 0.003 | 0
MAD-461-I | Addressable sounder with isolator |  | 0.0001769 | 0 | 0 | 0.00835 | 0
MAD-464-I Low Volume (78 dB) | Addressable sounder with isolator |  | 0.0001765 | 0 | 0 | 0.01232 | 0
MAD-464-I Medium Volume (93 dB) | Addressable sounder with isolator |  | 0.0001765 | 0 | 0 | 0.01232 | 0
MAD-464-I High Volume (97 dB) | Addressable sounder with isolator |  | 0.0001765 | 0 | 0 | 0.01232 | 0
MAD-465-I Low Volume (78 dB) | Addressable sounder with beacon and isolator |  | 0.0001773 | 0 | 0 | 0.01232 | 0
MAD-465-I Medium Volume (93 dB) | Addressable sounder with beacon and isolator |  | 0.0001773 | 0 | 0 | 0.01232 | 0
MAD-465-I High Volume (97 dB) | Addressable sounder with beacon and isolator |  | 0.0001773 | 0 | 0 | 0.01232 | 0
MAD-564-I (loop) | Addressable sounder with isolator |  | 0.00158 | 0 | 0 | 0.02111 | 0
MAD-564-I (External PS) | Addressable sounder with isolator |  | 0.00035 | 0 | 0 | 0.0008 | 0
MAD-565-I (loop) | Addressable sounder with VAD and isolator |  | 0.00158 | 0 | 0 | 0.03345 | 0
MAD-565-I (External PS) | Addressable sounder with VAD and isolator |  | 0.00035 | 0 | 0 | 0.0008 | 0
MAD-565-I - only flash (loop) | Addressable VAD with isolator |  | 0.00158 | 0 | 0 | 0.03345 | 0
MAD-565-I - only flash (External PS) | Addressable VAD with isolator |  | 0.00035 | 0 | 0 | 0.0008 | 0
MAD-567-I (loop) | Sounder base with isolator |  | 0.00117 | 0 | 0 | 0.00895 | 0
MAD-567-I (External PS) | Sounder base with isolator |  | 0.000261 | 0 | 0 | 0.00071 | 0
MAD-569-I (loop) | Sounder & VAD base with isolator |  | 0.00117 | 0 | 0 | 0.02326 | 0
MAD-569-I (External PS) | Sounder & VAD base with isolator |  | 0.0002589 | 0 | 0 | 0.00071 | 0
MAD-569-I - only flash (loop) | VAD base with isolator |  | 0.00117 | 0 | 0 | 0.02326 | 0
MAD-569-I only flash (External PS) | VAD base with isolator |  | 0.0002589 | 0 | 0 | 0.00071 | 0
MAD-472 | Sounder base |  | 0.0001074 | 0 | 0 | 0.00845 | 0
MAD-473 | Sounder base with flash |  | 0.0001068 | 0 | 0 | 0.00948 | 0
MAD-481 | 1 output 230V addressable module |  | 0.0003 | 0 | 0 | 0.003 | 0
MAD-481-I | 1 output 230V addressable module with isolator |  | 0.0003 | 0 | 0 | 0.003 | 0
MAD-490 | Isolator module |  | 6.96e-05 | 0 | 0 | 0.03766 | 0
PAD-10A-I | Remote indicator with isolator |  | 0.0001764 | 0 | 0 | 0.00298 | 0
TPLD-100 (CCD-102) = 3 loop address | 2 zones fire alarm control panel connected to loop |  | 0.001863 | 0 | 0 | 0.00186 | 0
TPLD-100 (CCD-104) = 5 loop address | 4 zones fire alarm control panel connected to loop |  | 0.001863 | 0 | 0 | 0.00186 | 0
TPLD-100 (CCD-108) = 9 loop address | 8 zones fire alarm control panel connected to loop |  | 0.001863 | 0 | 0 | 0.00186 | 0
TPLD-100 (CCD-112) = 13 loop address | 12 zones fire alarm control panel connected to loop |  | 0.001863 | 0 | 0 | 0.00186 | 0
TPLD-100 (CCD-103) = 7 loop address | Extinguishing control panel connected to loop |  | 0.001863 | 0 | 0 | 0.00186 | 0
Total |  | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
Loop Parameters
Cu | 0.0172 | Ω*mm2/m
I_Standby | 0 | A
I_Alarm | 0 | A
I_Sounders | 0 | A
I_Total | 0 | A
V_Lin_Ring | 6.9 | V
Minimum Cable Section for common Lenghts | [10 empty] | Warning: The Minimum Cable Seccion in the Loop is 0,5 mm2
Lenghts | 1000 | 1500 |  | 2000 |  |  | 2500 | 3000 | 3500 | m
R_Cable | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! | #DIV/0! | Ω
R_eq_Ring | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! | #DIV/0! | Ω
S_min | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | mm2
Maximum Cable Lenght for Standard Cable Section (IEC 60228) | [10 empty] | Warning: The Maximum Cable Length in the Loop is 3500 meters
Section | 0.5 | 0.75 |  | 1 |  |  | 1.5 | 2.5 | 4 | mm2
R_Cable | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! | #DIV/0! | Ω
R_eq_Ring | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! | #DIV/0! | Ω
L_max | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | m
Maximum Current Calculation
? S | 1.5 | mm2
? L | 1000 | mm2
R_Cable_Sys | 22.9333 | Ω
R_eq_Ring_Sys | 11.4667 | Ω
I_max | 0.60174 | A
System Check
Current |  | OK
Addresses |  | OK
This tool may be used as a design help for Detnov Security S.L. We reserve the right not to be responsible for its accuracy, completeness or quality of the information provided, including any kind of information which could be incomplete or incorrect.

## SC_Loop 6
SYSTEM CALCULATOR DETNOV CAD-150 EXCEL TOOL | [11 empty] | SC 116 en 2019 i
Loop | [9 empty] | System Check
Section of wire | 1.5 | 16 | [7 empty] | Current |  | OK
Lenght loop | 1000 | meters | [7 empty] | Addresses |  | OK
Fill Cable Section in mm2 and the Line Distance in meters (Yelow field)
|  | Fill the PCS field for the desired configuration (Yelow field) | Fill the PCS field for the desired configuration (Yelow field)
Devices Loop 6
REF. | Description | PCS | I_Standby (A) | I_Standby (A) | PCS_alarm | I_Alarm (A) | I_Alarm (A) | I_Sounders (A) | DET | MOD | SND | ADR
DOD-220A | Addressable smoke detector |  | 0.0001272 | 0 | 0 | 0.00361 | 0
DOD-220A-I | Addressable smoke detector with isolator |  | 0.0001958 | 0 | 0 | 0.00374 | 0
DOTD-230A | Addressable smoke and heat detector |  | 0.0001416 | 0 | 0 | 0.0036 | 0
DOTD-230A-I | Addressable smoke and heat detector with isolator |  | 0.0002124 | 0 | 0 | 0.00374 | 0
DTD-210A | Addressable heat detector |  | 0.0001222 | 0 | 0 | 0.00364 | 0
DTD-210A-I | Addressable heat detector with isolator |  | 0.0001924 | 0 | 0 | 0.00376 | 0
DTD-215A | Addressable high temperature detector |  | 0.0001337 | 0 | 0 | 0.00378 | 0
DTD-215A-I | Addressable high temperature detector with isolator |  | 0.0002035 | 0 | 0 | 0.00377 | 0
DGD-600 | Stand-alone natural gas detector (24V) |  | 0.00218 | 0 | 0 | 0.00222 | 0
DGD-600-AC | Stand-alone natural gas detector (230V) |  | 0.0026 | 0 | 0 | 0.00316 | 0
DGD-620 | Stand-alone LPG detector (24V) |  | 0.00218 | 0 | 0 | 0.00222 | 0
DGD-620-AC | Stand-alone LPG detector (230V) |  | 0.0026 | 0 | 0 | 0.00316 | 0
DBD-70A | Addressable lineal smoke detector |  | 0.038 | 0 | 0 | 0.038 | 0
MAD-401 & MAD-401-I | 1 output addressable module |  | 0.0002168 | 0 | 0 | 0.00306 | 0
MAD-402 & MAD-402-I | 2 outputs addressable module |  | 0.0002174 | 0 | 0 | 0.00595 | 0 |  |  | 0
MAD-405-I | 5 outputs addressable module |  | 0.0002786 | 0 | 0 | 0.00315 | 0 |  |  | 0
MAD-409-I | 10 outputs addressable module |  | 0.0003677 | 0 | 0 | 0.0033 | 0
MAD-411 & MAD-411-I | 1 input addressable module |  | 0.0001916 | 0 | 0 | 0.00306 | 0
MAD-412 & MAD-412-I | 2 inputs addressable module |  | 0.000191 | 0 | 0 | 0.00584 | 0 |  |  | 0
MAD-415-I | 5 inputs addressable module |  | 0.0001888 | 0 | 0 | 0.00395 | 0 |  |  | 0
MAD-419-I | 10 inputs addressable module |  | 0.0001892 | 0 | 0 | 0.00484 | 0 |  |  | 0
MAD-421 & MAD-421-I | 1 output/1 input addressable module |  | 0.0002101 | 0 | 0 | 0.00592 | 0 |  |  | 0
MAD-422 & MAD-422-I | 2 outputs/2 inputs addressable module |  | 0.000234 | 0 | 0 | 0.00591 | 0 |  |  | 0
MAD-425-I | 5 outputs/5 inputs addressable module |  | 0.000284 | 0 | 0 | 0.00408 | 0 |  |  | 0
MAD-429-I | 10 outputs/10 inputs addressable module |  | 0.0003766 | 0 | 0 | 0.005 | 0 |  |  | 0
MAD-431 & MAD-431-I | 1 output 24V addressable module |  | 0.000215 | 0 | 0 | 0.00361 | 0
MAD-432 & MAD-432-I | 2 outputs 24V addressable module |  | 0.0002033 | 0 | 0 | 0.0068 | 0
MAD-441 & MAD-441-I | 1 conventional zone addressable module |  | 0.0001878 | 0 | 0 | 0.00304 | 0
MAD-442 & MAD-442-I | 2 conventionals zones addressable module |  | 0.0001878 | 0 | 0 | 0.00584 | 0
MAD-450 & MAD-450-I | Addressable manual call point with isolator |  | 0.0001766 | 0 | 0 | 0.00303 | 0
MAD-451-I | Addressable manual call point with isolator |  | 0.0001774 | 0 | 0 | 0.003 | 0
MAD-461-I | Addressable sounder with isolator |  | 0.0001769 | 0 | 0 | 0.00835 | 0
MAD-464-I Low Volume (78 dB) | Addressable sounder with isolator |  | 0.0001765 | 0 | 0 | 0.01232 | 0
MAD-464-I Medium Volume (93 dB) | Addressable sounder with isolator |  | 0.0001765 | 0 | 0 | 0.01232 | 0
MAD-464-I High Volume (97 dB) | Addressable sounder with isolator |  | 0.0001765 | 0 | 0 | 0.01232 | 0
MAD-465-I Low Volume (78 dB) | Addressable sounder with beacon and isolator |  | 0.0001773 | 0 | 0 | 0.01232 | 0
MAD-465-I Medium Volume (93 dB) | Addressable sounder with beacon and isolator |  | 0.0001773 | 0 | 0 | 0.01232 | 0
MAD-465-I High Volume (97 dB) | Addressable sounder with beacon and isolator |  | 0.0001773 | 0 | 0 | 0.01232 | 0
MAD-564-I (loop) | Addressable sounder with isolator |  | 0.00158 | 0 | 0 | 0.02111 | 0
MAD-564-I (External PS) | Addressable sounder with isolator |  | 0.00035 | 0 | 0 | 0.0008 | 0
MAD-565-I (loop) | Addressable sounder with VAD and isolator |  | 0.00158 | 0 | 0 | 0.03345 | 0
MAD-565-I (External PS) | Addressable sounder with VAD and isolator |  | 0.00035 | 0 | 0 | 0.0008 | 0
MAD-565-I - only flash (loop) | Addressable VAD with isolator |  | 0.00158 | 0 | 0 | 0.03345 | 0
MAD-565-I - only flash (External PS) | Addressable VAD with isolator |  | 0.00035 | 0 | 0 | 0.0008 | 0
MAD-567-I (loop) | Sounder base with isolator |  | 0.00117 | 0 | 0 | 0.00895 | 0
MAD-567-I (External PS) | Sounder base with isolator |  | 0.000261 | 0 | 0 | 0.00071 | 0
MAD-569-I (loop) | Sounder & VAD base with isolator |  | 0.00117 | 0 | 0 | 0.02326 | 0
MAD-569-I (External PS) | Sounder & VAD base with isolator |  | 0.0002589 | 0 | 0 | 0.00071 | 0
MAD-569-I - only flash (loop) | VAD base with isolator |  | 0.00117 | 0 | 0 | 0.02326 | 0
MAD-569-I only flash (External PS) | VAD base with isolator |  | 0.0002589 | 0 | 0 | 0.00071 | 0
MAD-472 | Sounder base |  | 0.0001074 | 0 | 0 | 0.00845 | 0
MAD-473 | Sounder base with flash |  | 0.0001068 | 0 | 0 | 0.00948 | 0
MAD-481 | 1 output 230V addressable module |  | 0.0003 | 0 | 0 | 0.003 | 0
MAD-481-I | 1 output 230V addressable module with isolator |  | 0.0003 | 0 | 0 | 0.003 | 0
MAD-490 | Isolator module |  | 6.96e-05 | 0 | 0 | 0.03766 | 0
PAD-10A-I | Remote indicator with isolator |  | 0.0001764 | 0 | 0 | 0.00298 | 0
TPLD-100 (CCD-102) = 3 loop address | 2 zones fire alarm control panel connected to loop |  | 0.001863 | 0 | 0 | 0.00186 | 0
TPLD-100 (CCD-104) = 5 loop address | 4 zones fire alarm control panel connected to loop |  | 0.001863 | 0 | 0 | 0.00186 | 0
TPLD-100 (CCD-108) = 9 loop address | 8 zones fire alarm control panel connected to loop |  | 0.001863 | 0 | 0 | 0.00186 | 0
TPLD-100 (CCD-112) = 13 loop address | 12 zones fire alarm control panel connected to loop |  | 0.001863 | 0 | 0 | 0.00186 | 0
TPLD-100 (CCD-103) = 7 loop address | Extinguishing control panel connected to loop |  | 0.001863 | 0 | 0 | 0.00186 | 0
Total |  | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
Loop Parameters
Cu | 0.0172 | Ω*mm2/m
I_Standby | 0 | A
I_Alarm | 0 | A
I_Sounders | 0 | A
I_Total | 0 | A
V_Lin_Ring | 6.9 | V
Minimum Cable Section for common Lenghts | [10 empty] | Warning: The Minimum Cable Seccion in the Loop is 0,5 mm2
Lenghts | 1000 | 1500 |  | 2000 |  |  | 2500 | 3000 | 3500 | m
R_Cable | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! | #DIV/0! | Ω
R_eq_Ring | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! | #DIV/0! | Ω
S_min | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | mm2
Maximum Cable Lenght for Standard Cable Section (IEC 60228) | [10 empty] | Warning: The Maximum Cable Length in the Loop is 3500 meters
Section | 0.5 | 0.75 |  | 1 |  |  | 1.5 | 2.5 | 4 | mm2
R_Cable | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! | #DIV/0! | Ω
R_eq_Ring | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! | #DIV/0! | Ω
L_max | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | m
Maximum Current Calculation
? S | 1.5 | mm2
? L | 1000 | mm2
R_Cable_Sys | 22.9333 | Ω
R_eq_Ring_Sys | 11.4667 | Ω
I_max | 0.60174 | A
System Check
Current |  | OK
Addresses |  | OK
This tool may be used as a design help for Detnov Security S.L. We reserve the right not to be responsible for its accuracy, completeness or quality of the information provided, including any kind of information which could be incomplete or incorrect.

## SC_Loop 7
SYSTEM CALCULATOR DETNOV CAD-150 EXCEL TOOL | [11 empty] | SC 116 en 2019 i
Loop | [9 empty] | System Check
Section of wire | 1.5 | 16 | [7 empty] | Current |  | OK
Lenght loop | 1000 | meters | [7 empty] | Addresses |  | OK
Fill Cable Section in mm2 and the Line Distance in meters (Yelow field)
|  | Fill the PCS field for the desired configuration (Yelow field) | Fill the PCS field for the desired configuration (Yelow field)
Devices Loop 7
REF. | Description | PCS | I_Standby (A) | I_Standby (A) | PCS_alarm | I_Alarm (A) | I_Alarm (A) | I_Sounders (A) | DET | MOD | SND | ADR
DOD-220A | Addressable smoke detector |  | 0.0001272 | 0 | 0 | 0.00361 | 0
DOD-220A-I | Addressable smoke detector with isolator |  | 0.0001958 | 0 | 0 | 0.00374 | 0
DOTD-230A | Addressable smoke and heat detector |  | 0.0001416 | 0 | 0 | 0.0036 | 0
DOTD-230A-I | Addressable smoke and heat detector with isolator |  | 0.0002124 | 0 | 0 | 0.00374 | 0
DTD-210A | Addressable heat detector |  | 0.0001222 | 0 | 0 | 0.00364 | 0
DTD-210A-I | Addressable heat detector with isolator |  | 0.0001924 | 0 | 0 | 0.00376 | 0
DTD-215A | Addressable high temperature detector |  | 0.0001337 | 0 | 0 | 0.00378 | 0
DTD-215A-I | Addressable high temperature detector with isolator |  | 0.0002035 | 0 | 0 | 0.00377 | 0
DGD-600 | Stand-alone natural gas detector (24V) |  | 0.00218 | 0 | 0 | 0.00222 | 0
DGD-600-AC | Stand-alone natural gas detector (230V) |  | 0.0026 | 0 | 0 | 0.00316 | 0
DGD-620 | Stand-alone LPG detector (24V) |  | 0.00218 | 0 | 0 | 0.00222 | 0
DGD-620-AC | Stand-alone LPG detector (230V) |  | 0.0026 | 0 | 0 | 0.00316 | 0
DBD-70A | Addressable lineal smoke detector |  | 0.038 | 0 | 0 | 0.038 | 0
MAD-401 & MAD-401-I | 1 output addressable module |  | 0.0002168 | 0 | 0 | 0.00306 | 0
MAD-402 & MAD-402-I | 2 outputs addressable module |  | 0.0002174 | 0 | 0 | 0.00595 | 0 |  |  | 0
MAD-405-I | 5 outputs addressable module |  | 0.0002786 | 0 | 0 | 0.00315 | 0 |  |  | 0
MAD-409-I | 10 outputs addressable module |  | 0.0003677 | 0 | 0 | 0.0033 | 0
MAD-411 & MAD-411-I | 1 input addressable module |  | 0.0001916 | 0 | 0 | 0.00306 | 0
MAD-412 & MAD-412-I | 2 inputs addressable module |  | 0.000191 | 0 | 0 | 0.00584 | 0 |  |  | 0
MAD-415-I | 5 inputs addressable module |  | 0.0001888 | 0 | 0 | 0.00395 | 0 |  |  | 0
MAD-419-I | 10 inputs addressable module |  | 0.0001892 | 0 | 0 | 0.00484 | 0 |  |  | 0
MAD-421 & MAD-421-I | 1 output/1 input addressable module |  | 0.0002101 | 0 | 0 | 0.00592 | 0 |  |  | 0
MAD-422 & MAD-422-I | 2 outputs/2 inputs addressable module |  | 0.000234 | 0 | 0 | 0.00591 | 0 |  |  | 0
MAD-425-I | 5 outputs/5 inputs addressable module |  | 0.000284 | 0 | 0 | 0.00408 | 0 |  |  | 0
MAD-429-I | 10 outputs/10 inputs addressable module |  | 0.0003766 | 0 | 0 | 0.005 | 0 |  |  | 0
MAD-431 & MAD-431-I | 1 output 24V addressable module |  | 0.000215 | 0 | 0 | 0.00361 | 0
MAD-432 & MAD-432-I | 2 outputs 24V addressable module |  | 0.0002033 | 0 | 0 | 0.0068 | 0
MAD-441 & MAD-441-I | 1 conventional zone addressable module |  | 0.0001878 | 0 | 0 | 0.00304 | 0
MAD-442 & MAD-442-I | 2 conventionals zones addressable module |  | 0.0001878 | 0 | 0 | 0.00584 | 0
MAD-450 & MAD-450-I | Addressable manual call point with isolator |  | 0.0001766 | 0 | 0 | 0.00303 | 0
MAD-451-I | Addressable manual call point with isolator |  | 0.0001774 | 0 | 0 | 0.003 | 0
MAD-461-I | Addressable sounder with isolator |  | 0.0001769 | 0 | 0 | 0.00835 | 0
MAD-464-I Low Volume (78 dB) | Addressable sounder with isolator |  | 0.0001765 | 0 | 0 | 0.01232 | 0
MAD-464-I Medium Volume (93 dB) | Addressable sounder with isolator |  | 0.0001765 | 0 | 0 | 0.01232 | 0
MAD-464-I High Volume (97 dB) | Addressable sounder with isolator |  | 0.0001765 | 0 | 0 | 0.01232 | 0
MAD-465-I Low Volume (78 dB) | Addressable sounder with beacon and isolator |  | 0.0001773 | 0 | 0 | 0.01232 | 0
MAD-465-I Medium Volume (93 dB) | Addressable sounder with beacon and isolator |  | 0.0001773 | 0 | 0 | 0.01232 | 0
MAD-465-I High Volume (97 dB) | Addressable sounder with beacon and isolator |  | 0.0001773 | 0 | 0 | 0.01232 | 0
MAD-564-I (loop) | Addressable sounder with isolator |  | 0.00158 | 0 | 0 | 0.02111 | 0
MAD-564-I (External PS) | Addressable sounder with isolator |  | 0.00035 | 0 | 0 | 0.0008 | 0
MAD-565-I (loop) | Addressable sounder with VAD and isolator |  | 0.00158 | 0 | 0 | 0.03345 | 0
MAD-565-I (External PS) | Addressable sounder with VAD and isolator |  | 0.00035 | 0 | 0 | 0.0008 | 0
MAD-565-I - only flash (loop) | Addressable VAD with isolator |  | 0.00158 | 0 | 0 | 0.03345 | 0
MAD-565-I - only flash (External PS) | Addressable VAD with isolator |  | 0.00035 | 0 | 0 | 0.0008 | 0
MAD-567-I (loop) | Sounder base with isolator |  | 0.00117 | 0 | 0 | 0.00895 | 0
MAD-567-I (External PS) | Sounder base with isolator |  | 0.000261 | 0 | 0 | 0.00071 | 0
MAD-569-I (loop) | Sounder & VAD base with isolator |  | 0.00117 | 0 | 0 | 0.02326 | 0
MAD-569-I (External PS) | Sounder & VAD base with isolator |  | 0.0002589 | 0 | 0 | 0.00071 | 0
MAD-569-I - only flash (loop) | VAD base with isolator |  | 0.00117 | 0 | 0 | 0.02326 | 0
MAD-569-I only flash (External PS) | VAD base with isolator |  | 0.0002589 | 0 | 0 | 0.00071 | 0
MAD-472 | Sounder base |  | 0.0001074 | 0 | 0 | 0.00845 | 0
MAD-473 | Sounder base with flash |  | 0.0001068 | 0 | 0 | 0.00948 | 0
MAD-481 | 1 output 230V addressable module |  | 0.0003 | 0 | 0 | 0.003 | 0
MAD-481-I | 1 output 230V addressable module with isolator |  | 0.0003 | 0 | 0 | 0.003 | 0
MAD-490 | Isolator module |  | 6.96e-05 | 0 | 0 | 0.03766 | 0
PAD-10A-I | Remote indicator with isolator |  | 0.0001764 | 0 | 0 | 0.00298 | 0
TPLD-100 (CCD-102) = 3 loop address | 2 zones fire alarm control panel connected to loop |  | 0.001863 | 0 | 0 | 0.00186 | 0
TPLD-100 (CCD-104) = 5 loop address | 4 zones fire alarm control panel connected to loop |  | 0.001863 | 0 | 0 | 0.00186 | 0
TPLD-100 (CCD-108) = 9 loop address | 8 zones fire alarm control panel connected to loop |  | 0.001863 | 0 | 0 | 0.00186 | 0
TPLD-100 (CCD-112) = 13 loop address | 12 zones fire alarm control panel connected to loop |  | 0.001863 | 0 | 0 | 0.00186 | 0
TPLD-100 (CCD-103) = 7 loop address | Extinguishing control panel connected to loop |  | 0.001863 | 0 | 0 | 0.00186 | 0
Total |  | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
Loop Parameters
Cu | 0.0172 | Ω*mm2/m
I_Standby | 0 | A
I_Alarm | 0 | A
I_Sounders | 0 | A
I_Total | 0 | A
V_Lin_Ring | 6.9 | V
Minimum Cable Section for common Lenghts | [10 empty] | Warning: The Minimum Cable Seccion in the Loop is 0,5 mm2
Lenghts | 1000 | 1500 |  | 2000 |  |  | 2500 | 3000 | 3500 | m
R_Cable | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! | #DIV/0! | Ω
R_eq_Ring | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! | #DIV/0! | Ω
S_min | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | mm2
Maximum Cable Lenght for Standard Cable Section (IEC 60228) | [10 empty] | Warning: The Maximum Cable Length in the Loop is 3500 meters
Section | 0.5 | 0.75 |  | 1 |  |  | 1.5 | 2.5 | 4 | mm2
R_Cable | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! | #DIV/0! | Ω
R_eq_Ring | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! | #DIV/0! | Ω
L_max | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | m
Maximum Current Calculation
? S | 1.5 | mm2
? L | 1000 | mm2
R_Cable_Sys | 22.9333 | Ω
R_eq_Ring_Sys | 11.4667 | Ω
I_max | 0.60174 | A
System Check
Current |  | OK
Addresses |  | OK
This tool may be used as a design help for Detnov Security S.L. We reserve the right not to be responsible for its accuracy, completeness or quality of the information provided, including any kind of information which could be incomplete or incorrect.

## SC_Loop 8
SYSTEM CALCULATOR DETNOV CAD-150 EXCEL TOOL | [11 empty] | SC 116 en 2019 i
Loop | [9 empty] | System Check
Section of wire | 1.5 | 16 | [7 empty] | Current |  | OK
Lenght loop | 1000 | meters | [7 empty] | Addresses |  | OK
Fill Cable Section in mm2 and the Line Distance in meters (Yelow field)
|  | Fill the PCS field for the desired configuration (Yelow field) | Fill the PCS field for the desired configuration (Yelow field)
Devices Loop 8
REF. | Description | PCS | I_Standby (A) | I_Standby (A) | PCS_alarm | I_Alarm (A) | I_Alarm (A) | I_Sounders (A) | DET | MOD | SND | ADR
DOD-220A | Addressable smoke detector |  | 0.0001272 | 0 | 0 | 0.00361 | 0
DOD-220A-I | Addressable smoke detector with isolator |  | 0.0001958 | 0 | 0 | 0.00374 | 0
DOTD-230A | Addressable smoke and heat detector |  | 0.0001416 | 0 | 0 | 0.0036 | 0
DOTD-230A-I | Addressable smoke and heat detector with isolator |  | 0.0002124 | 0 | 0 | 0.00374 | 0
DTD-210A | Addressable heat detector |  | 0.0001222 | 0 | 0 | 0.00364 | 0
DTD-210A-I | Addressable heat detector with isolator |  | 0.0001924 | 0 | 0 | 0.00376 | 0
DTD-215A | Addressable high temperature detector |  | 0.0001337 | 0 | 0 | 0.00378 | 0
DTD-215A-I | Addressable high temperature detector with isolator |  | 0.0002035 | 0 | 0 | 0.00377 | 0
DGD-600 | Stand-alone natural gas detector (24V) |  | 0.00218 | 0 | 0 | 0.00222 | 0
DGD-600-AC | Stand-alone natural gas detector (230V) |  | 0.0026 | 0 | 0 | 0.00316 | 0
DGD-620 | Stand-alone LPG detector (24V) |  | 0.00218 | 0 | 0 | 0.00222 | 0
DGD-620-AC | Stand-alone LPG detector (230V) |  | 0.0026 | 0 | 0 | 0.00316 | 0
DBD-70A | Addressable lineal smoke detector |  | 0.038 | 0 | 0 | 0.038 | 0
MAD-401 & MAD-401-I | 1 output addressable module |  | 0.0002168 | 0 | 0 | 0.00306 | 0
MAD-402 & MAD-402-I | 2 outputs addressable module |  | 0.0002174 | 0 | 0 | 0.00595 | 0 |  |  | 0
MAD-405-I | 5 outputs addressable module |  | 0.0002786 | 0 | 0 | 0.00315 | 0 |  |  | 0
MAD-409-I | 10 outputs addressable module |  | 0.0003677 | 0 | 0 | 0.0033 | 0
MAD-411 & MAD-411-I | 1 input addressable module |  | 0.0001916 | 0 | 0 | 0.00306 | 0
MAD-412 & MAD-412-I | 2 inputs addressable module |  | 0.000191 | 0 | 0 | 0.00584 | 0 |  |  | 0
MAD-415-I | 5 inputs addressable module |  | 0.0001888 | 0 | 0 | 0.00395 | 0 |  |  | 0
MAD-419-I | 10 inputs addressable module |  | 0.0001892 | 0 | 0 | 0.00484 | 0 |  |  | 0
MAD-421 & MAD-421-I | 1 output/1 input addressable module |  | 0.0002101 | 0 | 0 | 0.00592 | 0 |  |  | 0
MAD-422 & MAD-422-I | 2 outputs/2 inputs addressable module |  | 0.000234 | 0 | 0 | 0.00591 | 0 |  |  | 0
MAD-425-I | 5 outputs/5 inputs addressable module |  | 0.000284 | 0 | 0 | 0.00408 | 0 |  |  | 0
MAD-429-I | 10 outputs/10 inputs addressable module |  | 0.0003766 | 0 | 0 | 0.005 | 0 |  |  | 0
MAD-431 & MAD-431-I | 1 output 24V addressable module |  | 0.000215 | 0 | 0 | 0.00361 | 0
MAD-432 & MAD-432-I | 2 outputs 24V addressable module |  | 0.0002033 | 0 | 0 | 0.0068 | 0
MAD-441 & MAD-441-I | 1 conventional zone addressable module |  | 0.0001878 | 0 | 0 | 0.00304 | 0
MAD-442 & MAD-442-I | 2 conventionals zones addressable module |  | 0.0001878 | 0 | 0 | 0.00584 | 0
MAD-450 & MAD-450-I | Addressable manual call point with isolator |  | 0.0001766 | 0 | 0 | 0.00303 | 0
MAD-451-I | Addressable manual call point with isolator |  | 0.0001774 | 0 | 0 | 0.003 | 0
MAD-461-I | Addressable sounder with isolator |  | 0.0001769 | 0 | 0 | 0.00835 | 0
MAD-464-I Low Volume (78 dB) | Addressable sounder with isolator |  | 0.0001765 | 0 | 0 | 0.01232 | 0
MAD-464-I Medium Volume (93 dB) | Addressable sounder with isolator |  | 0.0001765 | 0 | 0 | 0.01232 | 0
MAD-464-I High Volume (97 dB) | Addressable sounder with isolator |  | 0.0001765 | 0 | 0 | 0.01232 | 0
MAD-465-I Low Volume (78 dB) | Addressable sounder with beacon and isolator |  | 0.0001773 | 0 | 0 | 0.01232 | 0
MAD-465-I Medium Volume (93 dB) | Addressable sounder with beacon and isolator |  | 0.0001773 | 0 | 0 | 0.01232 | 0
MAD-465-I High Volume (97 dB) | Addressable sounder with beacon and isolator |  | 0.0001773 | 0 | 0 | 0.01232 | 0
MAD-564-I (loop) | Addressable sounder with isolator |  | 0.00158 | 0 | 0 | 0.02111 | 0
MAD-564-I (External PS) | Addressable sounder with isolator |  | 0.00035 | 0 | 0 | 0.0008 | 0
MAD-565-I (loop) | Addressable sounder with VAD and isolator |  | 0.00158 | 0 | 0 | 0.03345 | 0
MAD-565-I (External PS) | Addressable sounder with VAD and isolator |  | 0.00035 | 0 | 0 | 0.0008 | 0
MAD-565-I - only flash (loop) | Addressable VAD with isolator |  | 0.00158 | 0 | 0 | 0.03345 | 0
MAD-565-I - only flash (External PS) | Addressable VAD with isolator |  | 0.00035 | 0 | 0 | 0.0008 | 0
MAD-567-I (loop) | Sounder base with isolator |  | 0.00117 | 0 | 0 | 0.00895 | 0
MAD-567-I (External PS) | Sounder base with isolator |  | 0.000261 | 0 | 0 | 0.00071 | 0
MAD-569-I (loop) | Sounder & VAD base with isolator |  | 0.00117 | 0 | 0 | 0.02326 | 0
MAD-569-I (External PS) | Sounder & VAD base with isolator |  | 0.0002589 | 0 | 0 | 0.00071 | 0
MAD-569-I - only flash (loop) | VAD base with isolator |  | 0.00117 | 0 | 0 | 0.02326 | 0
MAD-569-I only flash (External PS) | VAD base with isolator |  | 0.0002589 | 0 | 0 | 0.00071 | 0
MAD-472 | Sounder base |  | 0.0001074 | 0 | 0 | 0.00845 | 0
MAD-473 | Sounder base with flash |  | 0.0001068 | 0 | 0 | 0.00948 | 0
MAD-481 | 1 output 230V addressable module |  | 0.0003 | 0 | 0 | 0.003 | 0
MAD-481-I | 1 output 230V addressable module with isolator |  | 0.0003 | 0 | 0 | 0.003 | 0
MAD-490 | Isolator module |  | 6.96e-05 | 0 | 0 | 0.03766 | 0
PAD-10A-I | Remote indicator with isolator |  | 0.0001764 | 0 | 0 | 0.00298 | 0
TPLD-100 (CCD-102) = 3 loop address | 2 zones fire alarm control panel connected to loop |  | 0.001863 | 0 | 0 | 0.00186 | 0
TPLD-100 (CCD-104) = 5 loop address | 4 zones fire alarm control panel connected to loop |  | 0.001863 | 0 | 0 | 0.00186 | 0
TPLD-100 (CCD-108) = 9 loop address | 8 zones fire alarm control panel connected to loop |  | 0.001863 | 0 | 0 | 0.00186 | 0
TPLD-100 (CCD-112) = 13 loop address | 12 zones fire alarm control panel connected to loop |  | 0.001863 | 0 | 0 | 0.00186 | 0
TPLD-100 (CCD-103) = 7 loop address | Extinguishing control panel connected to loop |  | 0.001863 | 0 | 0 | 0.00186 | 0
Total |  | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
Loop Parameters
Cu | 0.0172 | Ω*mm2/m
I_Standby | 0 | A
I_Alarm | 0 | A
I_Sounders | 0 | A
I_Total | 0 | A
V_Lin_Ring | 6.9 | V
Minimum Cable Section for common Lenghts | [10 empty] | Warning: The Minimum Cable Seccion in the Loop is 0,5 mm2
Lenghts | 1000 | 1500 |  | 2000 |  |  | 2500 | 3000 | 3500 | m
R_Cable | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! | #DIV/0! | Ω
R_eq_Ring | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! | #DIV/0! | Ω
S_min | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | mm2
Maximum Cable Lenght for Standard Cable Section (IEC 60228) | [10 empty] | Warning: The Maximum Cable Length in the Loop is 3500 meters
Section | 0.5 | 0.75 |  | 1 |  |  | 1.5 | 2.5 | 4 | mm2
R_Cable | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! | #DIV/0! | Ω
R_eq_Ring | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! | #DIV/0! | Ω
L_max | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | m
Maximum Current Calculation
? S | 1.5 | mm2
? L | 1000 | mm2
R_Cable_Sys | 22.9333 | Ω
R_eq_Ring_Sys | 11.4667 | Ω
I_max | 0.60174 | A
System Check
Current |  | OK
Addresses |  | OK
This tool may be used as a design help for Detnov Security S.L. We reserve the right not to be responsible for its accuracy, completeness or quality of the information provided, including any kind of information which could be incomplete or incorrect.